## Slide 1: Tackling Indoor Air Pollution Air Filtration
Peter Dyment
peter.dyment@camfil.com
www.camfil.co.uk
December 2021
CIBSE HVAC GROUP

## Slide 2
Outdoor (urban) air quality is a major health issue
Urban air quality is the top environmental risk factor for premature deaths in Europe Source: The State of Natural Capital report
Air pollution shortens the lives of more than 50,000 people in the UK every year
The WHO estimates the total annual cost of air
pollution to the UK economy at £53bn, or
3.7% of GDP
High air pollution also results in low birth weights, and has a negative impact on cognitive development
Risk to Health from
Traffic air pollution
NOx and PM1 2.5 10
SOx H2S O3 …..
Traffic air pollution PM1 and NO2 is a WHO group 1 carcinogen. No safe level of exposure.

## Slide 3
SARS-CoV-2
NEW - Covid19 virus size at 0.12mm to 0.16mm
Note: 1mm = 1 micron = 1 thousandth of a mm. Small
“In the mind of scientists working on this, there’s absolutely no doubt that the virus spreads in the air,” says aerosol scientist Lidia Morawska at the Queensland University of Technology in Brisbane, Australia. “This is a no-brainer.”
Mechanical Air Filtration has an important role in delivering clean indoor air into buildings
Air can also be cleaned by recirculation air cleaners and purifiers with tested air filters

## Slide 4
Autumn 2020
Last month 2021
This week 2021
Airborne transmission
Covid19 Particles in air
Face masks reduce Particles
Evolution of Government Covid19 guidance over time
is not defined but can be considered as outdoor air. It is not always clean air.
What about Winter cold?
can be infectious aerosols. Which particle size carries greatest risk of infection?
can be removed by air filters of the required filtration tested efficiency

## Slide 5
NEW WHO LIMITS
Changes deliberated over for 16 years by hundreds of the world’s top medical health experts with report supported by about 250 study papers
“Guidelines are applicable to both outdoor and indoor environments globally. Thus, they cover all settings where people spend time”.
Covid19 / Traffic
Traffic

## Slide 6
BS EN 16798-3:2017 IAQ Filter requirements
BS EN ISO 16890:2016 Particle filter testing
BS EN ISO 10121-2:2013 Molecular filter testing
Eurovent 4-23 (Oct 18) Supply Air filter requirements
WHO guidelines Air pollution exposure limits
The convergence of standards and guidelines now provides a means of selecting air filters to ensure healthy clean air for people to breathe inside city buildings – especially public buildings offices schools and hospitals
There has also been published IAQ guidance by Well Building, BREAM LEED and ASHRAE
https://eurovent.eu/?q=content/eurovent-423-2020-selection-en-iso-16890-rated-air-filter-classes-third-edition-english
https://apps.who.int/iris/handle/10665/345329
https://shop.bsigroup.com/products/energy-performance-of-buildings-ventilation-for-buildings-for-non-residential-buildings-performance-requirements-for-ventilation-and-room-conditioning-systems-modules-m5-1-m5-4/tracked-changes
https://shop.bsigroup.com/products/air-filters-for-general-ventilation-technical-specifications-requirements-and-classification-system-based-upon-particulate-matter-efficiency-epm/standard
https://landingpage.bsigroup.com/LandingPage/Series?UPI=BS%20EN%20ISO%2010121

## Slide 7: Using BS EN16798-3:2017 standard guidance to select correct air filtration efficiency
Based on the outdoor air (ODA) and supply air (SUP) categories, it is then possible to determine the required final filter efficiencies to achieve the specified clean indoor air
Outdoor Air |  |  | Supply Air |  |  |  | 
 |  |  | SUP1 IAQ | SUP2 IAQ | SUP3 | SUP4 | SUP5
 |  |  | PM2.5≤2.5µg/m3 PM10≤5µg/m3 | PM2.5≤5µg/m3 PM10≤10µg/m3 | PM2.5≤7.5µg/m3 PM10≤15µg/m3 | PM2.5≤10µg/m3 PM10≤20µg/m3 | PM2.5≤15µg/m3 PM10≤30µg/m3
Category | PM2.5 | PM10 | ePM1 a | ePM1 a | ePM2.5 b | ePM10 | ePM10
ODA1 | ≤10µg/m3 | ≤20µg/m3 | 70% a | 50% a | 50% a | 50% | 50%
ODA2 | ≤15µg/m3 | ≤30µg/m3 | 80% a | 70% a | 70% a | 80% | 50%
ODA3 | >15µg/m3 | >30µg/m3 | 90% a | 80% a | 80% a | 90% | 80%
a - minimum filtration requirements ISO ePM1 % refer to final filter stage
b - minimum filtration requirements ISO ePM2.5 % refer to final filter stage

## Slide 8
Core Recommendations for Covid19 and traffic air pollution with CO2 reduction (Energy efficiency)
Core Strategy proposal consists of delivering clean healthy indoor air by:
Utilizing and upgrading air filtration in existing mechanical ventilation systems where possible.(Existing legacy HVAC)
Total efficiency for supply side air filters upgraded to ePM1 80% minimum (WHO limit factors) (BS ISO16890)
Recirculation/Extract air filters upgraded to minimum ePM1 60% or better. (WHO limit factors) (BS ISO16890)
Use of low energy air filters (LEAF) for best energy efficiency and long life. CO2 reduction. (COP26)
Use of Hepa H14 class standalone air cleaners where main ventilation systems do not exist or are insufficient.
Maintenance – Monitor – Record data - Readjust
Use Air monitoring to confirm clean air benefits are being delivered. Use air monitor control function if possible.
https://www.ashrae.org/file%20library/technical%20resources/covid-19/core-recommendations-for-reducing-airborne-infectious-aerosol-exposure.pdf

## Slide 9
Addenbrookes Hospital Study
January 18th to February 5th 2021 - beds in the ward and ICU were at 100% occupancy
Results of control tests (No air filtration in operation)
We were able to detect SARS-CoV-2 on all sampling days; RNA was detected in both the medium (1-4μM) and the large (>4μM) particulate fractions.
SARS-CoV-2 RNA was not detected in the small (<1μM)
“Cleaner air will reduce the risk of airborne disease transmission”
Professor Stephen Baker, from the Cambridge Institute of Therapeutic Immunology and Infectious Disease at the University of Cambridge
https://www.cuh.nhs.uk/news/air-filters-on-wards-remove-almost-all-airborne-covid-virus/

## Slide 10
January 18th to February 5th 2021 - beds in the ward and ICU were at 100% occupancy
SARS-CoV-2 RNA was not detected in the small airborne particles (<1μM)
“Cleaner air will reduce the risk of airborne disease transmission”
Professor Stephen Baker, from the Cambridge Institute of Therapeutic Immunology and Infectious Disease at the University of Cambridge
Proposition:
If no Covid19 RNA was detected in any of the samples taken for particles
Below 1 micron (<1μM) then infection risk resides in particles above 1μM
Therefore:
ISO16890 tested HVAC filters class ePM1 to high efficiency are capable of removing infectious particles.This can be in any building ventilation system,office, school, home
Addenbrookes Hospital Study
When no air filtration was in operation
Particle size sampling
BC251 Aerosol Sampler

## Slide 11
These data are consistent with our observations, suggesting that aerosol precautions may be more important in conventional wards than in well defined ‘aerosol risk areas’.
Addenbrookes Hospital Study

## Slide 12
Addenbrookes Hospital Study
These data are consistent with our observations, suggesting that aerosol precautions may be more important in conventional wards than in well defined ‘aerosol risk areas’.

## Slide 13
NOTE: These two filters can be used as single stage system
BS EN ISO 16890:2016 gives accurate test data in the small particle size range
It also allows for calculation of multi stage AHU HVAC filter efficiency

## Slide 14
BS EN ISO 16890:2016 gives accurate test data in the small particle size range
It also allows for calculation of multi stage AHU HVAC filter efficiency
Outdoor Air
Indoor Air
Recirc Air damper
Example of HVAC AHU filter system effective at removing airborne aerosol particles
Supply Air
Recirc Air
20 deg.C?
0 deg.C?
Recirculation air cycle 5 airchanges per hour? (cycle time12 mins)
Single pass PM1 efficiency. (3stage)
Traffic air pollution etc
10 airchanges per hour? (cycle time 6 mins)
PM2.5 (3stage)
efficiency 99.2%
Note: recirculation of clean filtered air could reduce heating/cooling energy costs by up to 80% (legacy systems)

## Slide 15
Note: EN1822 and ISO29463 are related HEPA test standards

## Slide 16
Air purifier unit

## Slide 17
Proof that PM1 particles make deep lung penetration
Reference : Study by Karolinska Institute Stockholm

## Slide 18
Eurovent A+ rated filters
New BS EN ISO 16890:2016 tested labels

## Slide 19
Based on BS EN ISO 16890:2016

## Slide 20
Suggested WHO scores on the doors approach
advocated by independent SAGE Report 51
Has the advantage of staying in step with any
future changes made to WHO exposure limits.
Combines with traffic light system to give good visual display similar to Eurovent energy rating.
Uses mg/M3 generally as WHO limit reporting.
Air pollutant list can be expanded to suit.
https://www.independentsage.org/wp-content/uploads/2021/10/Ventilation-Certification-and-Ratings-FINAL-for-website-1.pdf

## Slide 22
Clean Healthy
Indoor Air at
Minimum cost
Clean Healthy Air - Control and demonstration of performance

## Slide 23
Core Recommendations for Covid19 and traffic air pollution with CO2 reduction (Energy efficiency)
Core Strategy proposal consists of delivering clean healthy indoor air by:
Utilizing and upgrading air filtration in existing mechanical ventilation systems where possible.(Existing legacy HVAC)
Total efficiency for supply side air filters upgraded to ePM1 80% minimum (WHO limit factors) (BS ISO16890)
Recirculation/Extract air filters upgraded to minimum ePM1 60% or better. (WHO limit factors) (BS ISO16890)
Use of low energy air filters (LEAF) for best energy efficiency and long life. CO2 reduction. (COP26)
Use of Hepa H14 class standalone air cleaners where main ventilation systems do not exist or are insufficient.
Maintenance – Monitor – Record data - Readjust
Use Air monitoring to confirm clean air benefits are being delivered. Use air monitor control function if possible.
https://www.ashrae.org/file%20library/technical%20resources/covid-19/core-recommendations-for-reducing-airborne-infectious-aerosol-exposure.pdf

## Slide 25
ISO 10121-1:2014 ISO101-2:2013
International Standard
Test method for assessing the 1.performance of gas phase media and 2.air cleaning devices for general ventilation (GPACD)
Testing based on four key parameters
Removal efficiency
Capacity
Retentivity
Operating pressure drop

## Slide 26
THANK YOU FOR YOUR ATTENTION
camfil
camfilgroup
camfil
camfilgroup
CLEAN AIR SOLUTIONS
www.camfil.com